Please note: all high voltage cables have been strictly inspected before shipping out of the factory, in accordance with following standards:

AC voltage ≤ 10KV, Testing Voltage: 3x Rating Voltage;

10KV ＜AC Voltage ≤20KV； Testing Voltage: 2x Rating Voltage

AC voltage ＞ 20KV Testing Voltage: 1.5x Rating Voltage

DC voltage ≤ 10KV, Testing Voltage: 1.5x Rating Voltage;

12KV ＜DC Voltage ≤20KV； Testing Voltage: 1.4x Rating Voltage

20KV ＜DC Voltage ≤30KV； Testing Voltage: 1.3x Rating Voltage

DC voltage ＞ 30KV Testing Voltage: 1.2x Rating Voltage

Disclaimer

The information given here is technical data, not assured product characteristics. It has been carefully checked and is believed to be accurate; however, no responsibility is assumed for inaccuracies. The user has to ensure by adequate tests that the product is suitable for his application regarding safety and technical aspects.

Shanghai Dingzun Electric & Cable Co., Ltd. does not assume any liability arising out of the application or use of any product described.